## Service Types
Main Service Type | Mergeable Service Types (separated by semicolons, can contain wildcards) | Merge Gap Tolerance (mm, default 0) | Apply to Compatibility Rule | Apply to Distance Rule | Apply to General Distance Rule | Apply to Support Rule | Apply to Report Rule | Apply to Angle Rule | Apply to Advanced Wall Distance Rule
Damper | Duct | 5 | x | x | x | x | x | x | x

## Service Distance
Service Types (separated by semicolons, can contain wildcards) | Distance with same Service Type (empty for unbounded) |  | Distance with different Service Types (empty for unbounded) |  | Issue Category (empty for default) | Note
| Minimum (mm) | Maximum (mm) | Minimum (mm) | Maximum (mm)
Cable Carrier | 100 |  | 100
Duc? | 100 |  | 100
Pipe | 100 |  | 100

## Service Compatibility
Service Type | Compatible Service Types (other than itself, separated by semicolons, can contain wildcards) | Note
Cable Carrier
Duct | Duct; --*
Pipe | *

## Fire Seal Proximity on Walls
Source Fire Seal Types (separated by semicolons, can contain wildcards) | Target Fire Seal Types (separated by semicolons, can contain wildcards) | Vertical Distance with other Fire Seals (mm) | Horizontal Distance with other Fire Seals (mm) | Issue Category (empty for default) | Note
Fire Seal Type Wall-3 | Fire Seal Type Wall-1 | 250 | 250 | Fire Seal Proximity
Fire Seal* | Fire Seal* | 299 | 300 | Fire Seal Proximity

## Fire Seal Proximity on Floors
Source Fire Seal Types (separated by semicolons, can contain wildcards) | Target Fire Seal Types (separated by semicolons, can contain wildcards) | Distance with other Fire Seals (mm) | Issue Category (empty for default) | Note
Fire Seal* | Fire Seal* | 300 | Fire Seal Proximity | Fire Seal Proximity

## Advanced Wall Proximity
Wall Types (separated by semicolons, can contain wildcards) | Source Fire Seal Types (separated by semicolons, can contain wildcards) | Target Fire Seal Types (separated by semicolons, can contain wildcards) | Vertical Distance with other Fire Seals (mm) | Horizontal Distance with other Fire Seals (mm) | Maximum Overhang (mm) | Issue Category (empty for default) | Note
Wall* | Fire Seal* | Fire Seal* | 300 | 300 | 1500 | Test

## Fire Seal and Service Distance
Fire Seal Types (separated by semicolons, can contain wildcards) | Allowed Service Types (separated by semicolons, can contain wildcards) | Distance between Services and Fire Seal edges (Floor Fire Seals only utilise the All Sides values ) |  |  |  |  | Issue Category (empty for default) | Note
|  | Minimum All Sides (mm) | Maximum All Sides (mm) | Minimum Top (mm) | Minimum Bottom (mm) | Minimum Sides (mm)
Fire Seal Type Wall-1 | Cable Carrier | 300 |  | 50 | 30 |  | Service to aperature
Fire Seal Type Wall-1 | *; --Cable Carrier | 300 |  |  |  |  | Service to aperature
Fire Seal Type Wall-2 | * | 300 |  | 50 | 30 |  | Service to aperature
Fire Seal Type Wall-3 | Pipe | 300 |  |  |  |  | Service to aperature

## Service Distance in Fire Seal
Fire Seal Types (separated by semicolons, can contain wildcards) | Source Service Types (separated by semicolons, can contain wildcards) | Target Service Types (separated by semicolons, can contain wildcards) | Distance between Source and Target Service Types (empty for unbounded) |  | Issue Category (empty for default) | Note
|  |  | Minimum (mm) | Maximum (mm)
Fire Seal Type Wall-1 | Cable Carrier | *; --Cable Carrier Special | 300 |  | Fire Seal Service to Service
Fire Seal Type Wall-1 | Cable Carrier | Cable Carrier Special | 50 |  | Fire Seal Service to Service
Fire Seal Type Wall-1 | *; --Cable Carrier | * | 300 |  | Fire Seal Service to Service
Fire Seal Type Wall-2 | * | * | 50 |  | Fire Seal Service to Service
Fire Seal Type Wall-3 | * | * | 300 |  | Fire Seal Service to Service

## Service Angle in Fire Seal
Fire Seal Types (separated by semicolons, can contain wildcards) | Service Types (separated by semicolons, can contain wildcards) | Angle Tolerance in Plan (degrees, empty for default) | Angle Tolerance in Elevation (degrees, empty for default) | Angle Limit in Plan (degrees, empty for default) | Angle Limit in Elevation (degrees, empty for default) | Issue Category (empty for default) | Note
Fire Seal* | Cable Carrier |  |  |  |  | Angle Check
Fire Seal* | *; --Cable Carrier |  |  |  |  | Angle Check

## Fire Seal Dimension
Fire Seal Types (separated by semicolons, can contain wildcards) | Minimum width (mm) | Maximum width (mm) | Minimum height (mm) | Maximum height (mm) | Issue Category (empty for default) | Note
Fire Seal* | 1600 | 2000 | 800 | 1600 | Fire Seal Dimensions

## Fire Seal Position on Walls
Fire Seal Types (separated by semicolons, can contain wildcards) | Distance with Side Compartmentations |  | Distance with Top Compartmentations |  |  | Distance with Bottom Compartmentations |  | Issue Category (empty for default) | Note
| Minimum (mm) | Offset (mm) | Minimum (mm) | Maximum (mm, empty for unbounded) | Offset (mm) | Minimum (mm) | Offset (mm)
Fire Seal* | 300 | 10 | 400 |  | 10 | 300 | 10 | Fire Seal position

## Fire Seal Position on Floors
Fire Seal Types (separated by semicolons, can contain wildcards) | Distance with Side Compartmentations |  | Issue Category (empty for default) | Note
| Minimum (mm) | Offset (mm)
Fire Seal* | 300 | 10 | Fire Seal Position

## Fire Seal Clearance on Walls
Fire Seal Types (separated by semicolons, can contain wildcards) | Side Offset (mm) | Top Offset (mm) | Depth (mm) | Bottom Tolerance (mm) | Bottom Depth (mm) | Issue Category (empty for default) | Note
Fire Seal Type Wall* | 500 | 500 | 500 | 300 | 1000 | Fire Seal Access / Installation Spatial Requirement

## Fire Seal Clearance on Floors
Fire Seal Types (separated by semicolons, can contain wildcards) | Offset (mm) | Height (mm) | Issue Category (empty for default) | Note
Fire Seal Type Floor* | 100 | 200 | Fire Seal Access / Installation Spatial Requirement

## Wall Support
Fire Seal Type (separated by semicolons, can contain wildcards) | Allowed Service Types (separated by semicolons, can contain wildcards) | Wall Type (separated by semicolons, can contain wildcards) | Width (empty for unbounded) |  | Fire Rate (empty for unbounded) |  | Acoustic Rate (empty for unbounded) |  | Deflection Movement (empty for unbounded) |  | Single/Double Sided (S/D) | Regular/Drop Head Detail (R/D) | Distance with Top Compartmentations (if Regular Detail) |  |  | Single/Multiple Service (S/M) | Perpendicular Service (P/NP) | Issue Category (empty for default) | Note
|  |  | Minimum (mm) | Maximum (mm) | Minimum (min) | Maximum (min) | Minimum (db) | Maximum (db) | Minimum (mm) | Maximum (mm) |  |  | Minimum (mm) | Maximum (mm, empty for unbounded) | Offset (mm)
Fire Seal 1 | Cable Carrier | Basic Wall* | 100 | 280 |  | 120 | 40 | 50 | 40 | 50 | D | D |  |  |  | S | P | Incompatible Wall Type
Fire Seal 1 | Cable Carrier* | Basic Wall* | 101 | 300 |  | 120 | 40 | 50 | 40 | 50 | D | D |  |  |  | S | P | Incompatible Wall Type
Fire Seal 1 | Cable Carrier | Basic Wall* | 101 | 300 |  | 120 | 40 | 50 | 40 | 50 | D | D |  |  |  | S | P | Incompatible Wall Type
Fire Seal* | *; --Cable Carrier | Basic Wall* | 100 | 600 |  |  |  |  | 40 | 50 | D | R | 100000 |  | 10 | M | P | Incompatible Wall Type
Fire Seal * | Cable Carrier | Basic Wall* | 100 | 300 |  |  |  |  | 30 | 240 | D | R | 300 |  | 10 | S | P | Incompatible Wall Type

## Classification Names
Solibri Fire Stopping Rule - Accessible Spaces | Solibri Firestopping Rule - Fire Seal Classification | Solibri Firestopping Rule - Service Classification | Solibri Firestopping Rule - Wall Classification
Accessible | Fire Seal Type Floor-1 | Cable Carrier | Basic Wall
Inaccessible | Fire Seal Type Wall-1 | Cable Carrier Special
| Fire Seal Type Wall-2 | Damper
| Fire Seal Type Wall-3 | Duct
Pipe